## Selector and Force Calculator
8954 | 0.53745 |  | CABLE CLEATS FORCE CALCULATOR* AND PRODUCT SELECTOR TOOL
according to the formula (B.7) from IEC 61914
Please enter the values in the gray cells
Product Selector Tool
Enter your cable outer diameter (O.D.): |  |  |  | 19 | mm
Select your preferred cable assembly formation from the drop down list: |  |  |  | Single Assembly
Select your preferred cable mounting configuration from the drop down list: |  |  |  | Flat Mount
Inserts required**: |  |  |  | With EPDM inserts
Search result: |  |  |  | CC15-26-FM
ET1062-000
Spacing and Force Calculator*
Peak short-circuit current value |  |  | Ip | 70 | kA
Center-to-center distance between two conductors*** |  |  | S | 50 | mm
Length of cable run |  |  |  | 100 | m
Calculated spacing between cable cleats lengthwise based on Ip |  |  | D | 0.5 | m
Total number of cable cleats on the cable run**** |  |  | N | 200 | pcs
Maximum force calculated* |  |  | Ft | 16660 | N/m
Notes
* | This calculator is configured to represent force calculations in accordance to Annex B of IEC 61914:2021.
** | Without inserts, the application range of the cable cleat can be extended up to 4mm. Refer to datasheet for details.
*** | Center-to-center distance "S" in trefoil configuration is the outer diameter of the cable.
**** | It is recommended to install 2-3 Cable Cleats at the start and the end of the cable run to increase the protection of the cable termination against potential fault condition. The recommended total number of cleats on the cable run does not include these additional cleats.
© 2025 TE Connectivity. All Rights Reserved. TE, TE Connectivity, TE connectivity (logo), EVERY CONNECTION COUNTS are trademarks owned or licensed by the TE Connectivity plc family of companies. Other product names, logos, and company names mentioned herein may be trademarks of their respective owners. The information given herein, including drawings, illustrations and schematics which are intended for illustration purposes only, is believed to be reliable. However, TE Connectivity makes no warranties as to its accuracy or completeness and disclaims any liability in connection with its use. TE Connectivity‘s obligations shall only be as set forth in TE Connectivity‘s Standard Terms and Conditions of Sale for this product and in no case will TE Connectivity be liable for any incidental, indirect or consequential damages arising out of the sale, resale, use or misuse of the product. Users of TE Connectivity products should make their own evaluation to determine the suitability of each such product for the specific application.
S=O.D.
S
S
D
𝑭_𝒕=(𝟎.𝟏𝟕 ∙〖𝒊_𝒑〗^𝟐)/𝑺

## Sheet1 (hidden)
| Part Desc | Part Number | Min range (minus 1mm for smallest) | Max range | Cleat Type | Mounting type | Insert | Hardware | Range Condition Met | Hardware Condition | Cleat Type Met | Insert Condition | Sum | Part Desc | Default+Type+Range | Default Force | Force | Report Ref#
ES8564-000 | CC15-26 | ES8564-000 | 18 | 30 | Single Assembly | Mounting hardware not required | No inserts | No | 1 | 0 | 1 | 0 | 2 | CC15-26 | 3 | 1 | 8954 | 14035/VNL
ES8565-000 | CC15-26-INS | ES8565-000 | 14 | 26 | Single Assembly | Mounting hardware not required | with EPDM inserts | No | 1 | 0 | 1 | 1 | 3 | CC15-26-INS | 3 | 1 | 8954 | 14035/VNL
ET1061-000 | CC15-26-SN | ET1061-000 | 14 | 26 | Single Assembly | Strut Nut | with EPDM inserts | Yes | 1 | 0 | 1 | 1 | 3 | CC15-26-SN | 2 | 0
ET1062-000 | CC15-26-FM | ET1062-000 | 14 | 26 | Single Assembly | Flat Mount | with EPDM inserts | Yes | 1 | 1 | 1 | 1 | 4 | CC15-26-FM | 2 | 0
ET1063-000 | CC15-26-CM | ET1063-000 | 14 | 26 | Single Assembly | Center Mount | with EPDM inserts | Yes | 1 | 0 | 1 | 1 | 3 | CC15-26-CM | 2 | 0
ER0001-000 | CC26-38 | ER0001-000 | 27 | 42 | Single Assembly | Mounting hardware not required | No inserts | No | 0 | 0 | 1 | 0 | 1 | CC26-38 | 2 | 1 | 20585.9 | 11452/VNL | Single Assembly | With EPDM inserts | Strut Nut
ER0002-000 | CC26-38-INS | ER0002-000 | 26 | 38 | Single Assembly | Mounting hardware not required | with EPDM inserts | No | 0 | 0 | 1 | 1 | 2 | CC26-38-INS | 2 | 1 |  |  | Dual Assembly | No inserts | Flat Mount
ER0003-000 | CC26-38-SN-M10 | ER0003-000 | [6 empty] | 0 | 0 | 0 | 0 | 0 | CC26-38-SN-M10 | 0 | 0 |  |  | Trefoil Assembly |  | Center Mount
ER0004-000 | CC26-38-SN | ER0004-000 | 26 | 38 | Single Assembly | Strut Nut | with EPDM inserts | Yes | 0 | 0 | 1 | 1 | 2 | CC26-38-SN | 1 | 0 |  |  |  |  | Mounting hardware not required
ER0005-000 | CC26-38-FM | ER0005-000 | 26 | 38 | Single Assembly | Flat Mount | with EPDM inserts | Yes | 0 | 1 | 1 | 1 | 3 | CC26-38-FM | 1 | 0
ER0006-000 | CC26-38-CM | ER0006-000 | 26 | 38 | Single Assembly | Center Mount | with EPDM inserts | Yes | 0 | 0 | 1 | 1 | 2 | CC26-38-CM | 1 | 0
ER0007-000 | CC26-38-SN-DOUB | ER0007-000 | [6 empty] | 0 | 0 | 0 | 0 | 0 | CC26-38-SN-DOUB | 0 | 0
ER0008-000 | CC26-38-FM-DOUB | ER0008-000 | [6 empty] | 0 | 0 | 0 | 0 | 0 | CC26-38-FM-DOUB | 0 | 0
ER0009-000 | CC26-38-SN-TRIP | ER0009-000 | [6 empty] | 0 | 0 | 0 | 0 | 0 | CC26-38-SN-TRIP | 0 | 0
ER0010-000 | CC38-50 | ER0010-000 | 39 | 54 | Single Assembly | Mounting hardware not required | No inserts | No | 0 | 0 | 1 | 0 | 1 | CC38-50 | 2 | 1 | 13350 | 13664-21-0083
ER0011-000 | CC38-50-INS | ER0011-000 | 38 | 50 | Single Assembly | Mounting hardware not required | with EPDM inserts | No | 0 | 0 | 1 | 1 | 2 | CC38-50-INS | 2 | 1
ER0012-000 | CC38-50-SN | ER0012-000 | 38 | 50 | Single Assembly | Strut Nut | with EPDM inserts | Yes | 0 | 0 | 1 | 1 | 2 | CC38-50-SN | 1 | 0
ER0013-000 | CC38-50-FM | ER0013-000 | 38 | 50 | Single Assembly | Flat Mount | with EPDM inserts | Yes | 0 | 1 | 1 | 1 | 3 | CC38-50-FM | 1 | 0
ER0014-000 | CC38-50-CM | ER0014-000 | 38 | 50 | Single Assembly | Center Mount | with EPDM inserts | Yes | 0 | 0 | 1 | 1 | 2 | CC38-50-CM | 1 | 0
ER0015-000 | CC38-50-SN-DOUB | ER0015-000 | [6 empty] | 0 | 0 | 0 | 0 | 0 | CC38-50-SN-DOUB | 0 | 0
ER0016-000 | CC38-50-FM-DOUB | ER0016-000 | [6 empty] | 0 | 0 | 0 | 0 | 0 | CC38-50-FM-DOUB | 0 | 0
ER0017-000 | CC38-50-SN-TRIP | ER0017-000 | [6 empty] | 0 | 0 | 0 | 0 | 0 | CC38-50-SN-TRIP | 0 | 0
ER0018-000 | CC50-75 | ER0018-000 | 51 | 79 | Single Assembly | Mounting hardware not required | No inserts | No | 0 | 0 | 1 | 0 | 1 | CC50-75 | 2 | 1 | 22300 | 13664-21-0085
ER0019-000 | CC50-75-INS | ER0019-000 | 50 | 75 | Single Assembly | Mounting hardware not required | with EPDM inserts | No | 0 | 0 | 1 | 1 | 2 | CC50-75-INS | 2 | 1
ER0020-000 | CC50-75-SN | ER0020-000 | 50 | 75 | Single Assembly | Strut Nut | with EPDM inserts | Yes | 0 | 0 | 1 | 1 | 2 | CC50-75-SN | 1 | 0
ER0021-000 | CC50-75-FM | ER0021-000 | 50 | 75 | Single Assembly | Flat Mount | with EPDM inserts | Yes | 0 | 1 | 1 | 1 | 3 | CC50-75-FM | 1 | 0
ER0022-000 | CC50-75-CM | ER0022-000 | 50 | 75 | Single Assembly | Center Mount | with EPDM inserts | Yes | 0 | 0 | 1 | 1 | 2 | CC50-75-CM | 1 | 0
ER0023-000 | CC50-75-SN-DOUB | ER0023-000 | [6 empty] | 0 | 0 | 0 | 0 | 0 | CC50-75-SN-DOUB | 0 | 0
ER0024-000 | CC50-75-FM-DOUB | ER0024-000 | [6 empty] | 0 | 0 | 0 | 0 | 0 | CC50-75-FM-DOUB | 0 | 0
ER0025-000 | CC50-75-SN-TRIP | ER0025-000 | [6 empty] | 0 | 0 | 0 | 0 | 0 | CC50-75-SN-TRIP | 0 | 0
ER0026-000 | CC75-100 | ER0026-000 | 76 | 104 | Single Assembly | Mounting hardware not required | No inserts | No | 0 | 0 | 1 | 0 | 1 | CC75-100 | 2 | 1 | 26033 | 12217/VNL
ER0027-000 | CC75-100-INS | ER0027-000 | 75 | 100 | Single Assembly | Mounting hardware not required | with EPDM inserts | No | 0 | 0 | 1 | 1 | 2 | CC75-100-INS | 2 | 1
ER0028-000 | CC75-100-SN | ER0028-000 | 75 | 100 | Single Assembly | Strut Nut | with EPDM inserts | Yes | 0 | 0 | 1 | 1 | 2 | CC75-100-SN | 1 | 0
ER0029-000 | CC75-100-FM | ER0029-000 | 75 | 100 | Single Assembly | Flat Mount | with EPDM inserts | Yes | 0 | 1 | 1 | 1 | 3 | CC75-100-FM | 1 | 0
ER0030-000 | CC75-100-CM | ER0030-000 | 75 | 100 | Single Assembly | Center Mount | with EPDM inserts | Yes | 0 | 0 | 1 | 1 | 2 | CC75-100-CM | 1 | 0
ER0031-000 | CC75-100-SN-DOUB | ER0031-000 | [6 empty] | 0 | 0 | 0 | 0 | 0 | CC75-100-SN-DOUB | 0 | 0
ER0032-000 | CC75-100-FM-DOUB | ER0032-000 | [6 empty] | 0 | 0 | 0 | 0 | 0 | CC75-100-FM-DOUB | 0 | 0
ER0033-000 | CC100-135 | ER0033-000 | 101 | 139 | Single Assembly | Mounting hardware not required | No inserts | No | 0 | 0 | 1 | 0 | 1 | CC100-135 | 2 | 1 | 32501 | 12219/VNL
ER0034-000 | CC100-135-INS | ER0034-000 | 100 | 135 | Single Assembly | Mounting hardware not required | with EPDM inserts | No | 0 | 0 | 1 | 1 | 2 | CC100-135-INS | 2 | 1
ER0035-000 | CC100-135-SN | ER0035-000 | 100 | 135 | Single Assembly | Strut Nut | with EPDM inserts | Yes | 0 | 0 | 1 | 1 | 2 | CC100-135-SN | 1 | 0
ER0036-000 | CC100-135-FM | ER0036-000 | 100 | 135 | Single Assembly | Flat Mount | with EPDM inserts | Yes | 0 | 1 | 1 | 1 | 3 | CC100-135-FM | 1 | 0
ER0037-000 | CC100-135-CM | ER0037-000 | 100 | 135 | Single Assembly | Center Mount | with EPDM inserts | Yes | 0 | 0 | 1 | 1 | 2 | CC100-135-CM | 1 | 0
ER0038-000 | CC100-135-SN-DOUB | ER0038-000 | [6 empty] | 0 | 0 | 0 | 0 | 0 | CC100-135-SN-DOUB | 0 | 0
ER0039-000 | CC100-135-FM-DOUB | ER0039-000 | [6 empty] | 0 | 0 | 0 | 0 | 0 | CC100-135-FM-DOUB | 0 | 0
ES8480-000 | CC135-175 | ES8480-000 | 139 | 179 | Single Assembly | Mounting hardware not required | No inserts | No | 0 | 0 | 1 | 0 | 1 | CC135-175 | 2 | 1 | Contact your Sales rep.
ES8481-000 | CC135-175-INS | ES8481-000 | 135 | 175 | Single Assembly | Mounting hardware not required | with EPDM inserts | No | 0 | 0 | 1 | 1 | 2 | CC135-175-INS | 2 | 1
ET1070-000 | CC135-175-FM | ET1070-000 | 135 | 175 | Single Assembly | Flat Mount | with EPDM inserts | Yes | 0 | 1 | 1 | 1 | 3 | CC135-175-FM | 1 | 0
ES8483-000 | CC175-220 | ES8483-000 | 179 | 224 | Single Assembly | Mounting hardware not required | No inserts | No | 0 | 0 | 1 | 0 | 1 | CC175-220 | 2 | 1 | Contact your Sales rep.
ES8484-000 | CC175-220-INS | ES8484-000 | 175 | 220 | Single Assembly | Mounting hardware not required | with EPDM inserts | No | 0 | 0 | 1 | 1 | 2 | CC175-220-INS | 2 | 1
ET1071-000 | CC175-220-FM | ET1071-000 | 175 | 220 | Single Assembly | Flat Mount | with EPDM inserts | Yes | 0 | 1 | 1 | 1 | 3 | CC175-220-FM | 1 | 0
ES8503-000 | CCD15-26 | ES8503-000 | 18 | 30 | Dual Assembly | Mounting hardware not required | No inserts | No | 1 | 0 | 0 | 0 | 1 | CCD15-26 | 2 | 1 | Contact your Sales rep.
ES8504-000 | CCD15-26-INS | ES8504-000 | 14 | 26 | Dual Assembly | Mounting hardware not required | with EPDM inserts | No | 1 | 0 | 0 | 1 | 2 | CCD15-26-INS | 2 | 1
ET1064-000 | CCD15-26-SN | ET1064-000 | 14 | 26 | Dual Assembly | Strut Nut | with EPDM inserts | Yes | 1 | 0 | 0 | 1 | 2 | CCD15-26-SN | 1 | 0
ET1065-000 | CCD15-26-FM | ET1065-000 | 14 | 26 | Dual Assembly | Flat Mount | with EPDM inserts | Yes | 1 | 1 | 0 | 1 | 3 | CCD15-26-FM | 1 | 0
ET1066-000 | CCD15-26-CM | ET1066-000 | 14 | 26 | Dual Assembly | Center Mount | with EPDM inserts | Yes | 1 | 0 | 0 | 1 | 2 | CCD15-26-CM | 1 | 0
ET1944-000 | CCD15-26-SN-DOUB | ET1944-000 | [6 empty] | 0 | 0 | 0 | 0 | 0 | CCD15-26-SN-DOUB | 0 | 0
ET1946-000 | CCD15-26-FM-DOUB | ET1946-000 | [6 empty] | 0 | 0 | 0 | 0 | 0 | CCD15-26-FM-DOUB | 0 | 0
ER0040-000 | CCD26-38 | ER0040-000 | 27 | 42 | Dual Assembly | Mounting hardware not required | No inserts | No | 0 | 0 | 0 | 0 | 0 | CCD26-38 | 1 | 1 | Contact your Sales rep.
ER0041-000 | CCD26-38-INS | ER0041-000 | 26 | 38 | Dual Assembly | Mounting hardware not required | with EPDM inserts | No | 0 | 0 | 0 | 1 | 1 | CCD26-38-INS | 1 | 1
ER0042-000 | CCD26-38-SN-M10 | ER0042-000 | [6 empty] | 0 | 0 | 0 | 0 | 0 | CCD26-38-SN-M10 | 0 | 0
ER0043-000 | CCD26-38-SN | ER0043-000 | 26 | 38 | Dual Assembly | Strut Nut | with EPDM inserts | Yes | 0 | 0 | 0 | 1 | 1 | CCD26-38-SN | 0 | 0
ER0044-000 | CCD26-38-FM | ER0044-000 | 26 | 38 | Dual Assembly | Flat Mount | with EPDM inserts | Yes | 0 | 1 | 0 | 1 | 2 | CCD26-38-FM | 0 | 0
ER0045-000 | CCD26-38-CM | ER0045-000 | 26 | 38 | Dual Assembly | Center Mount | with EPDM inserts | Yes | 0 | 0 | 0 | 1 | 1 | CCD26-38-CM | 0 | 0
ER0046-000 | CCD26-38-SN-DOUB | ER0046-000 | [6 empty] | 0 | 0 | 0 | 0 | 0 | CCD26-38-SN-DOUB | 0 | 0
ER0047-000 | CCD26-38-FM-DOUB | ER0047-000 | [6 empty] | 0 | 0 | 0 | 0 | 0 | CCD26-38-FM-DOUB | 0 | 0
ER0048-000 | CCD38-50 | ER0048-000 | 39 | 54 | Dual Assembly | Mounting hardware not required | No inserts | No | 0 | 0 | 0 | 0 | 0 | CCD38-50 | 1 | 1 | Contact your Sales rep.
ER0049-000 | CCD38-50-INS | ER0049-000 | 38 | 50 | Dual Assembly | Mounting hardware not required | with EPDM inserts | No | 0 | 0 | 0 | 1 | 1 | CCD38-50-INS | 1 | 1
ER0050-000 | CCD38-50-SN | ER0050-000 | 38 | 50 | Dual Assembly | Strut Nut | with EPDM inserts | Yes | 0 | 0 | 0 | 1 | 1 | CCD38-50-SN | 0 | 0
ER0051-000 | CCD38-50-FM | ER0051-000 | 38 | 50 | Dual Assembly | Flat Mount | with EPDM inserts | Yes | 0 | 1 | 0 | 1 | 2 | CCD38-50-FM | 0 | 0
ER0052-000 | CCD38-50-CM | ER0052-000 | 38 | 50 | Dual Assembly | Center Mount | with EPDM inserts | Yes | 0 | 0 | 0 | 1 | 1 | CCD38-50-CM | 0 | 0
ER0053-000 | CCD38-50-SN-DOUB | ER0053-000 | [6 empty] | 0 | 0 | 0 | 0 | 0 | CCD38-50-SN-DOUB | 0 | 0
ER0054-000 | CCD38-50-FM-DOUB | ER0054-000 | [6 empty] | 0 | 0 | 0 | 0 | 0 | CCD38-50-FM-DOUB | 0 | 0
ER0055-000 | CCD50-63 | ER0055-000 | 54 | 67 | Dual Assembly | Mounting hardware not required | No inserts | No | 0 | 0 | 0 | 0 | 0 | CCD50-63 | 1 | 1 | Contact your Sales rep.
ER0056-000 | CCD50-63-INS | ER0056-000 | 50 | 63 | Dual Assembly | Mounting hardware not required | with EPDM inserts | No | 0 | 0 | 0 | 1 | 1 | CCD50-63-INS | 1 | 1
ER0058-000 | CCD50-63-SN | ER0058-000 | 50 | 63 | Dual Assembly | Strut Nut | with EPDM inserts | Yes | 0 | 0 | 0 | 1 | 1 | CCD50-63-SN | 0 | 0
ER0059-000 | CCD50-63-FM | ER0059-000 | 50 | 63 | Dual Assembly | Flat Mount | with EPDM inserts | Yes | 0 | 1 | 0 | 1 | 2 | CCD50-63-FM | 0 | 0
ER0060-000 | CCD50-63-CM | ER0060-000 | 50 | 63 | Dual Assembly | Center Mount | with EPDM inserts | Yes | 0 | 0 | 0 | 1 | 1 | CCD50-63-CM | 0 | 0
ER0061-000 | CCD50-63-SN-DOUB | ER0061-000 | [6 empty] | 0 | 0 | 0 | 0 | 0 | CCD50-63-SN-DOUB | 0 | 0
ER0062-000 | CCD50-63-FM-DOUB | ER0062-000 | [6 empty] | 0 | 0 | 0 | 0 | 0 | CCD50-63-FM-DOUB | 0 | 0
ER0063-000 | CCD63-75 | ER0063-000 | 67 | 79 | Dual Assembly | Mounting hardware not required | No inserts | No | 0 | 0 | 0 | 0 | 0 | CCD63-75 | 1 | 1 | Contact your Sales rep.
ER0064-000 | CCD63-75-INS | ER0064-000 | 63 | 75 | Dual Assembly | Mounting hardware not required | with EPDM inserts | No | 0 | 0 | 0 | 1 | 1 | CCD63-75-INS | 1 | 1
ER0065-000 | CCD63-75-SN | ER0065-000 | 63 | 75 | Dual Assembly | Strut Nut | with EPDM inserts | Yes | 0 | 0 | 0 | 1 | 1 | CCD63-75-SN | 0 | 0
ER0066-000 | CCD63-75-FM | ER0066-000 | 63 | 75 | Dual Assembly | Flat Mount | with EPDM inserts | Yes | 0 | 1 | 0 | 1 | 2 | CCD63-75-FM | 0 | 0
ER0067-000 | CCD63-75-CM | ER0067-000 | 63 | 75 | Dual Assembly | Center Mount | with EPDM inserts | Yes | 0 | 0 | 0 | 1 | 1 | CCD63-75-CM | 0 | 0
ER0068-000 | CCD63-75-SN-DOUB | ER0068-000 | [6 empty] | 0 | 0 | 0 | 0 | 0 | CCD63-75-SN-DOUB | 0 | 0
ER0069-000 | CCD63-75-FM-DOUB | ER0069-000 | [6 empty] | 0 | 0 | 0 | 0 | 0 | CCD63-75-FM-DOUB | 0 | 0
ES8508-000 | CCD75-89 | ES8508-000 | 79 | 93 | Dual Assembly | Mounting hardware not required | No inserts | No | 0 | 0 | 0 | 0 | 0 | CCD75-89 | 1 | 1 | Contact your Sales rep.
ES8509-000 | CCD75-89-INS | ES8509-000 | 75 | 89 | Dual Assembly | Mounting hardware not required | with EPDM inserts | No | 0 | 0 | 0 | 1 | 1 | CCD75-89-INS | 1 | 1
ET1074-000 | CCD75-89-SN | ET1074-000 | 75 | 89 | Dual Assembly | Strut Nut | with EPDM inserts | Yes | 0 | 0 | 0 | 1 | 1 | CCD75-89-SN | 0 | 0
ET1075-000 | CCD75-89-FM | ET1075-000 | 75 | 89 | Dual Assembly | Flat Mount | with EPDM inserts | Yes | 0 | 1 | 0 | 1 | 2 | CCD75-89-FM | 0 | 0
ES8512-000 | CCD75-89-CM | ES8512-000 | 75 | 89 | Dual Assembly | Center Mount | with EPDM inserts | Yes | 0 | 0 | 0 | 1 | 1 | CCD75-89-CM | 0 | 0
ES8513-000 | CCD89-104 | ES8513-000 | 93 | 108 | Dual Assembly | Mounting hardware not required | No inserts | No | 0 | 0 | 0 | 0 | 0 | CCD89-104 | 1 | 1 | Contact your Sales rep.
ES8514-000 | CCD89-104-INS | ES8514-000 | 89 | 104 | Dual Assembly | Mounting hardware not required | with EPDM inserts | No | 0 | 0 | 0 | 1 | 1 | CCD89-104-INS | 1 | 1
ES8515-000 | CCD89-104-SN | ES8515-000 | 89 | 104 | Dual Assembly | Strut Nut | with EPDM inserts | Yes | 0 | 0 | 0 | 1 | 1 | CCD89-104-SN | 0 | 0
ET1077-000 | CCD89-104-FM | ET1077-000 | 89 | 104 | Dual Assembly | Flat Mount | with EPDM inserts | Yes | 0 | 1 | 0 | 1 | 2 | CCD89-104-FM | 0 | 0
ES8517-000 | CCD104-120 | ES8517-000 | 108 | 124 | Dual Assembly | Mounting hardware not required | No inserts | No | 0 | 0 | 0 | 0 | 0 | CCD104-120 | 0 | 0
ES8518-000 | CCD104-120-INS | ES8518-000 | 104 | 120 | Dual Assembly | Mounting hardware not required | with EPDM inserts | No | 0 | 0 | 0 | 1 | 1 | CCD104-120-INS | 0 | 0
ET1079-000 | CCD104-120-FM | ET1079-000 | 104 | 120 | Dual Assembly | Flat Mount | with EPDM inserts | Yes | 0 | 1 | 0 | 1 | 2 | CCD104-120-FM | 0 | 0
ES8486-000 | CCT15-26 | ES8486-000 | 18 | 30 | Trefoil Assembly | Mounting hardware not required | No inserts | No | 1 | 0 | 0 | 0 | 1 | CCT15-26 | 2 | 1 | 18536 | 14036/VNL
ES8487-000 | CCT15-26-INS | ES8487-000 | 14 | 26 | Trefoil Assembly | Mounting hardware not required | with EPDM inserts | No | 1 | 0 | 0 | 1 | 2 | CCT15-26-INS | 2 | 1
ET1067-000 | CCT15-26-SN | ET1067-000 | 14 | 26 | Trefoil Assembly | Strut Nut | with EPDM inserts | Yes | 1 | 0 | 0 | 1 | 2 | CCT15-26-SN | 1 | 0
ET1068-000 | CCT15-26-FM | ET1068-000 | 14 | 26 | Trefoil Assembly | Flat Mount | with EPDM inserts | Yes | 1 | 1 | 0 | 1 | 3 | CCT15-26-FM | 1 | 0
ET1069-000 | CCT15-26-CM | ET1069-000 | 14 | 26 | Trefoil Assembly | Center Mount | with EPDM inserts | Yes | 1 | 0 | 0 | 1 | 2 | CCT15-26-CM | 1 | 0
ER0070-000 | CCT26-38 | ER0070-000 | 27 | 42 | Trefoil Assembly | Mounting hardware not required | No inserts | No | 0 | 0 | 0 | 0 | 0 | CCT26-38 | 1 | 1 | 37733 | 11454/VNL
ER0071-000 | CCT26-38-INS | ER0071-000 | 26 | 38 | Trefoil Assembly | Mounting hardware not required | with EPDM inserts | No | 0 | 0 | 0 | 1 | 1 | CCT26-38-INS | 1 | 1
ER0072-000 | CCT26-38-SN-M10 | ER0072-000 | [6 empty] | 0 | 0 | 0 | 0 | 0 | CCT26-38-SN-M10 | 0 | 0
ER0074-000 | CCT26-38-SN | ER0074-000 | 26 | 38 | Trefoil Assembly | Strut Nut | with EPDM inserts | Yes | 0 | 0 | 0 | 1 | 1 | CCT26-38-SN | 0 | 0
ER0075-000 | CCT26-38-FM | ER0075-000 | 26 | 38 | Trefoil Assembly | Flat Mount | with EPDM inserts | Yes | 0 | 1 | 0 | 1 | 2 | CCT26-38-FM | 0 | 0
ER0076-000 | CCT26-38-CM | ER0076-000 | 26 | 38 | Trefoil Assembly | Center Mount | with EPDM inserts | Yes | 0 | 0 | 0 | 1 | 1 | CCT26-38-CM | 0 | 0
ER1990-000 | CCT26-38-SN-DOUB | ER1990-000 | [6 empty] | 0 | 0 | 0 | 0 | 0 | CCT26-38-SN-DOUB | 0 | 0
ER1991-000 | CCT26-38-FM-DOUB | ER1991-000 | [6 empty] | 0 | 0 | 0 | 0 | 0 | CCT26-38-FM-DOUB | 0 | 0
ER0077-000 | CCT38-50 | ER0077-000 | 39 | 54 | Trefoil Assembly | Mounting hardware not required | No inserts | No | 0 | 0 | 0 | 0 | 0 | CCT38-50 | 1 | 1 | 37206 | 12211/VNL
ER0078-000 | CCT38-50-INS | ER0078-000 | 38 | 50 | Trefoil Assembly | Mounting hardware not required | with EPDM inserts | No | 0 | 0 | 0 | 1 | 1 | CCT38-50-INS | 1 | 1
ER0079-000 | CCT38-50-SN | ER0079-000 | 38 | 50 | Trefoil Assembly | Strut Nut | with EPDM inserts | Yes | 0 | 0 | 0 | 1 | 1 | CCT38-50-SN | 0 | 0
ER0080-000 | CCT38-50-FM | ER0080-000 | 38 | 50 | Trefoil Assembly | Flat Mount | with EPDM inserts | Yes | 0 | 1 | 0 | 1 | 2 | CCT38-50-FM | 0 | 0
ER0081-000 | CCT38-50-CM | ER0081-000 | 38 | 50 | Trefoil Assembly | Center Mount | with EPDM inserts | Yes | 0 | 0 | 0 | 1 | 1 | CCT38-50-CM | 0 | 0
ER1992-000 | CCT38-50-SN-DOUB | ER1992-000 | [6 empty] | 0 | 0 | 0 | 0 | 0 | CCT38-50-SN-DOUB | 0 | 0
ER1993-000 | CCT38-50-FM-DOUB | ER1993-000 | [6 empty] | 0 | 0 | 0 | 0 | 0 | CCT38-50-FM-DOUB | 0 | 0
ER0082-000 | CCT50-63 | ER0082-000 | 54 | 67 | Trefoil Assembly | Mounting hardware not required | No inserts | No | 0 | 0 | 0 | 0 | 0 | CCT50-63 | 1 | 1 | 44580 | 12214/VNL
ER0083-000 | CCT50-63-INS | ER0083-000 | 50 | 63 | Trefoil Assembly | Mounting hardware not required | with EPDM inserts | No | 0 | 0 | 0 | 1 | 1 | CCT50-63-INS | 1 | 1
ER0084-000 | CCT50-63-SN | ER0084-000 | 50 | 63 | Trefoil Assembly | Strut Nut | with EPDM inserts | Yes | 0 | 0 | 0 | 1 | 1 | CCT50-63-SN | 0 | 0
ER0085-000 | CCT50-63-FM | ER0085-000 | 50 | 63 | Trefoil Assembly | Flat Mount | with EPDM inserts | Yes | 0 | 1 | 0 | 1 | 2 | CCT50-63-FM | 0 | 0
ER0086-000 | CCT50-63-CM | ER0086-000 | 50 | 63 | Trefoil Assembly | Center Mount | with EPDM inserts | Yes | 0 | 0 | 0 | 1 | 1 | CCT50-63-CM | 0 | 0
ER1994-000 | CCT50-63-SN-DOUB | ER1994-000 | [6 empty] | 0 | 0 | 0 | 0 | 0 | CCT50-63-SN-DOUB | 0 | 0
ER1995-000 | CCT50-63-FM-DOUB | ER1995-000 | [6 empty] | 0 | 0 | 0 | 0 | 0 | CCT50-63-FM-DOUB | 0 | 0
ER0087-000 | CCT63-75 | ER0087-000 | 67 | 79 | Trefoil Assembly | Mounting hardware not required | No inserts | No | 0 | 0 | 0 | 0 | 0 | CCT63-75 | 1 | 1 | 43310 | 12215/VNL
ER0088-000 | CCT63-75-INS | ER0088-000 | 63 | 75 | Trefoil Assembly | Mounting hardware not required | with EPDM inserts | No | 0 | 0 | 0 | 1 | 1 | CCT63-75-INS | 1 | 1
ER0089-000 | CCT63-75-SN | ER0089-000 | 63 | 75 | Trefoil Assembly | Strut Nut | with EPDM inserts | Yes | 0 | 0 | 0 | 1 | 1 | CCT63-75-SN | 0 | 0
ER0090-000 | CCT63-75-FM | ER0090-000 | 63 | 75 | Trefoil Assembly | Flat Mount | with EPDM inserts | Yes | 0 | 1 | 0 | 1 | 2 | CCT63-75-FM | 0 | 0
ER0091-000 | CCT63-75-CM | ER0091-000 | 63 | 75 | Trefoil Assembly | Center Mount | with EPDM inserts | Yes | 0 | 0 | 0 | 1 | 1 | CCT63-75-CM | 0 | 0
ER5436-000 | CCT26-38-POLE | ER5436-000 | [6 empty] | 0 | 0 | 0 | 0 | 0 | CCT26-38-POLE | 0 | 0
ES8491-000 | CCT75-89 | ES8491-000 | 79 | 93 | Trefoil Assembly | Mounting hardware not required | No inserts | No | 0 | 0 | 0 | 0 | 0 | CCT75-89 | 1 | 1 | 46269 | 14040/VNL
ES8492-000 | CCT75-89-INS | ES8492-000 | 75 | 89 | Trefoil Assembly | Mounting hardware not required | with EPDM inserts | No | 0 | 0 | 0 | 1 | 1 | CCT75-89-INS | 1 | 1
ET1072-000 | CCT75-89-SN | ET1072-000 | 75 | 89 | Trefoil Assembly | Strut Nut | with EPDM inserts | Yes | 0 | 0 | 0 | 1 | 1 | CCT75-89-SN | 0 | 0
ET1073-000 | CCT75-89-FM | ET1073-000 | 75 | 89 | Trefoil Assembly | Flat Mount | with EPDM inserts | Yes | 0 | 1 | 0 | 1 | 2 | CCT75-89-FM | 0 | 0
ES8495-000 | CCT75-89-CM | ES8495-000 | 75 | 89 | Trefoil Assembly | Center Mount | with EPDM inserts | Yes | 0 | 0 | 0 | 1 | 1 | CCT75-89-CM | 0 | 0
ES8496-000 | CCT89-104 | ES8496-000 | 93 | 108 | Trefoil Assembly | Mounting hardware not required | No inserts | No | 0 | 0 | 0 | 0 | 0 | CCT89-104 | 1 | 1 | 45568 | 14041/VNL
ES8497-000 | CCT89-104-INS | ES8497-000 | 89 | 104 | Trefoil Assembly | Mounting hardware not required | with EPDM inserts | No | 0 | 0 | 0 | 1 | 1 | CCT89-104-INS | 1 | 1
ES8498-000 | CCT89-104-SN | ES8498-000 | 89 | 104 | Trefoil Assembly | Strut Nut | with EPDM inserts | Yes | 0 | 0 | 0 | 1 | 1 | CCT89-104-SN | 0 | 0
ET1076-000 | CCT89-104-FM | ET1076-000 | 89 | 104 | Trefoil Assembly | Flat Mount | with EPDM inserts | Yes | 0 | 1 | 0 | 1 | 2 | CCT89-104-FM | 0 | 0
ES8500-000 | CCT104-120 | ES8500-000 | 108 | 124 | Trefoil Assembly | Mounting hardware not required | No inserts | No | 0 | 0 | 0 | 0 | 0 | CCT104-120 | 1 | 1 | 43238 | 14043/VNL
ES8501-000 | CCT104-120-INS | ES8501-000 | 104 | 120 | Trefoil Assembly | Mounting hardware not required | with EPDM inserts | No | 0 | 0 | 0 | 1 | 1 | CCT104-120-INS | 1 | 1
ET1078-000 | CCT104-120-FM | ET1078-000 | 104 | 120 | Trefoil Assembly | Flat Mount | with EPDM inserts | Yes | 0 | 1 | 0 | 1 | 2 | CCT104-120-FM | 0 | 0